## Slide 1
LA CCTV SUPPLY · PUBLIC BRIEFING
Understanding
SCIF & SAPF
Security
ICD 705, the IC Tech Spec and UL 2050 Extent 3: how secure spaces are approved, built and protected.
Public-level training · September 2026
Notes: Welcome. This briefing is a public-level introduction to how Sensitive Compartmented Information Facilities (SCIFs) and Special Access Program Facilities (SAPFs) are approved, built and protected. We will follow the documents that govern the work: ICD 705, its two standards, the IC Technical Specification version 1.5.1, and UL 2050 for intrusion detection. We will spend extra time on the parts low-voltage teams touch most: alarms, access control, penetrations, filters and shielding. Everything here comes from publicly released sources. Nothing replaces the written direction of your Accrediting Official, your Cognizant Security Authority or your Certified TEMPEST Technical Authority. When in doubt, ask them.

## Slide 2
02 · WHY THIS MATTERS
Why this matters
Sources: ICD 705 · DoDM 5105.21 Vol. 2 · UFC 4-010-05 (2023)
02 / 24
THE ONE IDEA
The approval, not the construction, makes it a SCIF.
A room built “to ICD 705” but never accredited is just an expensive room. SCI can’t be discussed or brought in until the Accrediting Official (AO) accredits the space.
Most failures trace back to steps skipped at the start.
WHO NEEDS ONE
Intelligence Community elements and DoD
Anyone handling Sensitive Compartmented Information (SCI) needs an accredited SCIF.
Cleared contractors
A government sponsor is required; DoD SCIFs need a SCIF number or written concept approval.
Special Access Programs
SAP work happens in a SAPF, accredited by a SAPF Accrediting Official.
WHO HAS TO GET IT RIGHT
Owners & sponsors
Architects & engineers
General contractors
Low-voltage integrators
Security managers
Notes: Why does any of this matter? Because a SCIF is defined by an approval, not by a construction method. ICD 705 requires that SCI be handled only in accredited facilities, and DoD guidance says SCI will not be discussed or introduced until the facility is accredited. Three groups need these spaces: Intelligence Community elements and DoD organizations, cleared contractors with a government sponsor, and Special Access Programs, which use SAPFs. Many people have to get the details right: owners, architects, general contractors, low-voltage integrators and security managers. The most expensive failures usually come from skipping early steps, such as talking to the AO after design is finished.

## Slide 3
03 · KNOW THE DIFFERENCE
SCIF vs SAPF vs open storage area vs GSA container
Sources: IC Tech Spec v1.5.1 · DoDM 5205.07 (2025) · 32 CFR 117.15 · 32 CFR 2001.43 · DCSA SAP checklist
03 / 24
 | SCIF | SAPF | NISPOM open storage area | GSA-approved container
Protects | Sensitive Compartmented Information (SCI) | Special Access Program information | Collateral classified (contractors) | Collateral; SCI only inside a closed storage SCIF
Rules | ICD 705 · ICS 705-1/-2 · IC Tech Spec | DoDM 5205.07 · Tech Spec criteria | 32 CFR 117 (NISPOM) · 32 CFR 2001 | 32 CFR 2001.43 · DoD Lock Program
Approved by | IC element AO (DIA for most DoD) | SAPF Accrediting Official | DCSA | Container must be GSA-approved
Intrusion detection | UL 2050 Extent 3 | UL 2050 Extent 3 | Extent 3 baseline; Extent 5 only with CSA approval | No IDS sensors on the container itself
Top Secret alarm response | Closed: 15 min · Open: 15 min with SID, 5 without | Same as SCIF | Open storage: 15 min with SID, 5 without | 2-hour checks, or IDS + 15 min, or SID + FF-L-2740 lock
Trap: a DCSA-approved open storage area is not a SCIF. Moving SAP into a SCIF, or SCI into a SAPF, needs a Co-Use Agreement first.
Notes: Four ways classified information is protected are often confused. A SCIF protects SCI under ICD 705 and is accredited by an Intelligence Community AO; for most of DoD and its contractors that is DIA. A SAPF protects Special Access Program information under DoDM 5205.07 and is accredited by a SAPF Accrediting Official. A NISPOM open storage area protects collateral classified material for contractors and is approved by DCSA. A GSA-approved container is storage equipment, not a facility. SCIFs and SAPFs both require UL 2050 Extent 3 alarm installations. Response times shown are the published Top Secret baselines; many items are left to AO or CSA determination, and exceeding a published standard requires a waiver. And remember: a SCIF accreditation does not automatically authorize SAP work.

## Slide 4
04 · GOVERNANCE
The document stack and current versions
Sources: ODNI/NCSC governance page · UL Standards catalog · eCFR · DoD issuances
04 / 24
DIRECTIVE
ICD 705
26 May 2010
STANDARD
ICS 705-1 · physical & technical
17 Sep 2010
STANDARD
ICS 705-2 · accreditation & reciprocity
22 Dec 2016
BUILD-TO SPEC
IC Tech Spec for ICD/ICS 705
v1.5.1 · 26 Jul 2021
DOD SCI MANUAL
DoDM 5105.21 Vol. 2
Change 2 · 2 Nov 2020
DOD SAP MANUAL
DoDM 5205.07 (Vol. 3 cancelled)
17 Jan 2025
DESIGN CRITERIA
UFC 4-010-05
26 May 2023
ALARM STANDARD
UL 2050
Edition 6 · 7 Apr 2025
COLLATERAL RULES
32 CFR 117 (NISPOM) · 32 CFR 2001
Current eCFR
Read down
for authority: what must be true
Read up
for method: how to build it
VERSION TRAP
“The 2020 Tech Spec” is out of date: v1.5.1 replaced v1.5 and moved the forms to Chapter 14.
When layers disagree, the stricter rule and your AO’s written direction win.
IC
DoD
UL
CFR
Notes: Here is the document stack with the current public versions. ICD 705 is the directive. ICS 705-1 sets the physical and technical standards, and ICS 705-2 covers accreditation and reciprocity. The IC Tech Spec, version 1.5.1 from July 2021, is the build-to document with the checklists and plans. DoD adds DoDM 5105.21 for SCI and the consolidated DoDM 5205.07 for SAP; Volume 3 was cancelled in January 2025. UFC 4-010-05 gives DoD design criteria, UL 2050 Edition 6 governs the alarm installation, and 32 CFR Parts 117 and 2001 cover collateral work. Read down for authority and up for method. When layers disagree, the stricter requirement and your AO’s written direction win.

## Slide 5
05 · ROLES
Who approves what
Sources: ICD 705 · ICS 705-1/-2 · IC Tech Spec 3.A · DoDM 5205.07 · UFC 4-010-05
05 / 24
DECIDERS
Approve
Accrediting Official (AO)
Approves design, CSP and final design; accredits the SCIF
SAPF Accrediting Official
Approves SAPF plans and accreditation
Cognizant Security Authority
Oversight and co-use concurrence
CTTA
Recommends countermeasures; AO approves
Authority Having Jurisdiction
Building code, fire and accessibility
SECURITY STAFF
Plan and run
Site Security Manager (SSM)
Owns security through construction; writes the Construction Security Plan (CSP)
SSO / SSR / CSSO
Run the accredited space every day: SOPs, logs, change reports
CSTs and escorts
Construction surveillance and site access control
TSCM team
Technical surveillance countermeasures, as required
BUILDERS
Produce evidence
Architect-engineer
Drawings and project data for the SSM
General contractor
Builds to approved drawings and CSP; keeps the photo record
IDS / low-voltage integrator
UL 2050 certificate, spec sheets and acceptance test results
Builders never approve their own work. Authority flows down from the IC element head; evidence flows up to the AO.
Notes: Every SCIF project involves three groups. Deciders approve: the AO approves the design concept, the Construction Security Plan and the final design, and accredits the facility; a SAPF Accrediting Official does the same for SAP. The CSA provides oversight and co-use concurrence. The CTTA recommends TEMPEST countermeasures, but the AO approves them. The AHJ owns life safety. Security staff plan and run the space: the Site Security Manager through construction, and the SSO, SSR or contractor CSSO once it is operating. Builders produce evidence: drawings, construction records and, for integrators, the UL 2050 certificate and test results. Waiver authority stays with the IC element head or a named senior official, never the AO.

## Slide 6
06 · ACCREDITATION LIFECYCLE
Six phases, each with a security gate
Sources: IC Tech Spec 2.A, 3.A–3.B · ICS 705-2 · UFC 4-010-05 · practitioner synthesis
06 / 24
PHASE 0
Sponsorship
OUTPUTS
Sponsor, AO and SSM identified; site feasibility
GATE
Security begins when the need is known
PHASE 1
Planning
OUTPUTS
Concept approval; Pre-Construction and TEMPEST checklists
GATE
AO and CTTA engaged before design is final
PHASE 2
Design
OUTPUTS
Drawings; door, penetration and IDS designs
GATE
AO approves the design and the CSP
PHASE 3
Award
OUTPUTS
Vetted team; long-lead orders placed
GATE
No contract award without an approved CSP
PHASE 4
Construction
OUTPUTS
Site controls; photo record; pre-cover inspection
GATE
SSM inspections; violations go to the AO
PHASE 5
Accreditation
OUTPUTS
IDS and acoustic tests; UL 2050 certificate; final checklist
GATE
AO inspection and letter of accreditation
AFTER ACCREDITATION
Operations and continuous monitoring
Re-evaluation at least every five years
Re-accreditation after major changes
Notes: Accreditation is a lifecycle, not a certificate at the end of construction. Phase 0 confirms the sponsor, the AO and a buildable site; the Tech Spec says security begins when the requirement is known. Phase 1 gets concept approval and the Pre-Construction and TEMPEST checklists to the AO and CTTA. Phase 2 produces the design, which the AO approves along with the Construction Security Plan. Phase 3 is award, and no contract should be awarded without an approved CSP. Phase 4 is construction under surveillance, with a photo record. Phase 5 is testing and inspection, ending in the letter of accreditation. After that come continuous monitoring, re-evaluation at least every five years, and re-accreditation after major changes.

## Slide 7
07 · FACILITY MODES
Facility modes and Security-in-Depth
Sources: IC Tech Spec 2.B, 3.C, 3.H · UFC 4-010-05 1-12 · FFC v1.5 Section B
07 / 24
MODE
SCI STORED
WALL
RESPONSE
Closed storage
In GSA containers
Wall A
15 min
Open storage + SID
In the open
Wall A
15 min
Open storage, no SID
In the open
Wall B or C
5 min
Continuous operation
Staffed 24/7
Wall A
Per AO
Secure Working Area
Not stored
Wall A
15 min
Response = initial alarm response force for facilities inside the U.S. (Tech Spec 3.H). With AO-accepted SID, open storage can use Wall A and a 15-minute response.
COMPOUND OR INSTALLATION
CONTROLLED BUILDING
ALARMED OFFICE AREA
SCIF
Layers that detect an intruder before the SCIF wall
The AO decides. SID is recorded in FFC Section B, and it is mandatory outside the U.S.
Notes: A SCIF’s mode drives walls, alarms and cost. Closed storage keeps all SCI in GSA-approved containers. Open storage lets SCI sit in the open, which raises the stakes. Continuous operation means staffed around the clock. A Secure Working Area allows discussion and processing but no storage. Security-in-Depth, or SID, is the credit a SCIF gets for protection around it: a controlled compound, a controlled building, or alarmed office space. The Tech Spec defines SID as factors that improve the chance of detection before anyone reaches the SCIF. With AO-accepted SID, open storage can use the standard Wall A and a 15-minute response. Without it, you need an enhanced wall and a 5-minute response. SID is mandatory overseas.

## Slide 8
08 · ANATOMY
Anatomy of a SCIF
Illustrative, not to scale. Countermeasures and approvals are set by your AO and CTTA.
08 / 24
1
2
3
4
5
6
7
8
9
10
11
12
13
14
1
Perimeter, slab to slab
2
Primary door + FF-L-2740 lock
3
Card reader + PIN
4
Door switch, UL 634 Level II
5
Motion sensors
6
IDS control unit + 24 h power
7
Vestibule + PED lockers
8
Duct over 96 sq in: bars
9
Penetration panel + filter
10
Sound masking
11
RED vs BLACK equipment
12
Fiber entry, no copper
13
Egress-only door, alarmed
14
Compartmented area
Notes: This cutaway pulls the whole topic into one picture. The perimeter (1) runs from true floor to true ceiling. The primary door (2) has an FF-L-2740 combination lock on FF-L-2890 hardware, with a card reader and PIN (3) outside and a UL 634 Level II door switch (4). Motion sensors (5) and the intrusion detection control unit with 24-hour standby power (6) sit inside. People leave phones in lockers in the vestibule (7). Large ducts get bars (8), and utilities enter at a single penetration panel with filtering (9). Sound masking (10) protects conversations. RED and BLACK equipment (11) stay apart, data arrives on fiber (12), the emergency exit (13) is alarmed, and a compartmented area (14) is separately controlled.

## Slide 9
09 · PERIMETER CONSTRUCTION
Perimeter walls: A, B and C
Sources: IC Tech Spec v1.5.1 §3.C and Figures 1–3 · UFC 4-010-05
09 / 24
← UNCONTROLLED SIDE
SCIF SIDE →
⅝ in. GWB
outside
Studs + track
16 gauge
Acoustic fill
3½ in.
⅝ in. GWB
inside, 1
⅝ in. GWB
inside, 2
EVERY WALL TYPE SHARES
True floor to true ceiling, painted
16-ga track in acoustical sealant
3½ in. acoustic fill
Staggered board seams
Wall A · Standard
SOUND GROUP 3
Three layers of ⅝ in. gypsum board: one outside, two on the SCIF side.
Use: closed storage, SWA, continuous ops, open storage with SID
Wall B · Enhanced
FORCED-ENTRY LAYER
Wall A plus #9 expanded metal on the SCIF side of the studs.
Use: open storage without SID (5-minute response)
Wall C · Enhanced
FORCED-ENTRY LAYER
½ in. plywood on the SCIF side under one board layer; two layers outside.
Use: open storage without SID (5-minute response)
Notes: The Tech Spec gives three perimeter wall details. Wall A is the standard: three layers of five-eighths gypsum board, one on the outside and two on the SCIF side, over 16-gauge studs with acoustic fill. It is designed for Sound Group 3. Walls B and C add a forced-entry layer: expanded metal on the SCIF side of the studs for Wall B, or half-inch plywood on the SCIF side for Wall C. The enhanced walls are for open storage without Security-in-Depth. Every type runs from true floor to true ceiling with continuous track bedded in acoustical sealant, staggered seams and a painted finish, so any cut or patch is visible. A common rework item is installing the hardening layer on the wrong side.

## Slide 10
10 · DOORS AND LOCKS
Doors and locks: three layers, two jobs
Sources: IC Tech Spec 3.E · FF-L-2740B · FF-L-2890C and QPL · ICS 705-1 §G.2.b · UFC 4-010-05 3-4.6.5
10 / 24
OUTSIDE VIEW
1
2
3
4
4 UL 634 Level II door switch
1
FF-L-2740B combination lock
Secures the empty SCIF. 20 man-hours surreptitious entry resistance; at least 1,000,000 combinations. Current models: Kaba Mas X-10, S&G 2740B.
2
FF-L-2890C lock extension
Ten device types: primary doors use Types I–IV, secondary VII–VIII, exit-only IX–X. Buy only from the current QPL, and check with the AHJ first.
3
Access control, duty hours only
At least two technologies, such as card + PIN, with a UL 1034 fail-secure strike. Never used to secure an unoccupied SCIF.
PRIMARY
One per SCIF; visitor control happens here
SECONDARY
Needs AO approval; ACS off when unoccupied
EMERGENCY EXIT
No outside hardware; alarmed 24/7
Notes: A SCIF primary door has three layers doing two jobs. When the SCIF is empty, an FF-L-2740B combination lock throws the deadbolt of an FF-L-2890 lock extension, and the alarm is armed. The current approved locks are the Kaba Mas X-10 and the Sargent and Greenleaf 2740B. FF-L-2890C defines ten device types; match the type to the door category and buy only from the Qualified Products List after checking with the fire marshal. During duty hours, access control with at least two technologies, such as card plus PIN, controls the latch through a UL 1034 fail-secure strike. Card readers never secure an unoccupied SCIF, and magnetic locks that release on power loss conflict with the fail-secure requirement.

## Slide 11
11 · PENETRATIONS
Penetrations: size, bars and a single point of entry
Sources: IC Tech Spec 3.G.1–3.G.7 · UFC 4-010-05 3-4.11, 3-4.12
11 / 24
96 sq in
Vent or duct openings larger than this need permanently affixed bars or grilles…
< 6 in.
…unless one dimension is under six inches.
WORKED EXAMPLES
12 × 10 in. = 120 sq in
Bars required
24 × 5 in. = 120 sq in
No bars: 5 in. side
8 × 8 in. = 64 sq in
No bars: under 96
12 × 8 in. = 96 sq in
No bars: not over 96
DUCT OPENING AT THE PERIMETER
Man-bars: ½ in. steel, welded both ways at 6 in. on center
Or: expanded metal, welded wire fabric, or metal baffles 6 in. apart
Every crossing is a problem to solve on paper first
Utilities enter at a single point; nothing for other areas transits the SCIF
Spare conduit filled with acoustic fill and capped
Bars don’t stop sound: every duct still needs acoustic treatment
Notes: Every duct, pipe and conduit through the perimeter is a potential path for sound, entry or signals. Tech Spec 3.G.7 sets the size rule: any vent or duct opening larger than 96 square inches gets permanently affixed bars or grilles, unless one dimension is under six inches. A 12 by 10 inch duct needs bars; 24 by 5 does not; exactly 96 does not, because the rule says exceeds. Bars are half-inch steel welded both ways at six inches on center, or approved mesh or baffles. Size exemptions never remove the acoustic treatment. Plan utilities to enter at a single point, keep other building services from passing through, and fill and cap any spare conduit.

## Slide 12
12 · ACOUSTICS
Acoustics: Sound Group 3 vs Sound Group 4
Sources: UFC 4-010-05 3-4.3 · IC Tech Spec Ch. 9 (as quoted by practitioners) · ASTM E90 / E413 / E336
12 / 24
SOUND GROUP 3
STC 45
FIELD TEST
NIC 40
LAB-RATED PARTS
STC 50
“Loud speech … can be faintly heard but not understood outside the SCIF.”
Default SCIF perimeter · Wall A
SOUND GROUP 4
STC 50
FIELD TEST
NIC 45
LAB-RATED PARTS
STC 55
“Very loud sounds … such as … a radio at full volume, can be heard … faintly or not at all outside the SCIF.”
VTC, conference and amplified-audio rooms
SOUND MASKING, WHEN THE AO APPROVES IT
Generator fixed inside the SCIF
No AM/FM receiver; recording disabled
Volume set by listening outside
Notes: Acoustic protection keeps conversations from being understood outside. STC is a laboratory rating for a wall or door; NIC is what a tester measures in the finished building, including flanking paths over walls, under doors and through ducts. Sound Group 3, STC 45 or NIC 40 in the field, is the default perimeter: loud speech may be heard faintly but not understood. Sound Group 4, STC 50 or NIC 45, applies where amplified audio is used, such as VTC and conference rooms. DoD criteria call for components rated higher in the lab, STC 50 and 55. If the AO approves sound masking, the generator stays inside the SCIF, has no radio receiver or recording, and is set by listening outside.

## Slide 13
13 · INTRUSION DETECTION
IDS essentials: the numbers every installer should know
Sources: IC Tech Spec 3.H (v1.5.1) and Ch. 7 (as quoted from the public v1.4 copy; confirm against v1.5.1). Some values allow AO-approved alternatives.
13 / 24
Extent 3
UL 2050 installation level
7.A.2.b
Level II
UL 634 switch and motion at each perimeter door
7.A.2.d
≤ 30 s
Entry delay at the primary door
7.A.3.a(6)
24 h
Uninterruptible backup power
7.B.5
15 min
Response force; 5 min for open storage without SID
3.H
60 min
SCI-indoctrinated person on site, or AO-approved time
7.C.1.c
≤ 1
False alarm per 30 days per IDS partition
7.A.2.p
4 h
Service must start after a trouble signal
7.C.2
Also: semiannual testing · IDS separate from fire and other systems · IDS alarms outrank access control events · control unit inside the SCIF
Notes: These are the numbers every IDS installer should know, from Tech Spec 3.H (v1.5.1) and Chapter 7 as quoted from the public v1.4 copy — confirm Chapter 7 against v1.5.1. The installation is UL 2050 Extent 3. Every perimeter door gets a UL 634 Level II high-security switch and motion detection. Entry delay at the primary door is 30 seconds or less. Backup power runs 24 hours. The response force arrives in 15 minutes, or 5 minutes for open storage without Security-in-Depth, and an SCI-indoctrinated person arrives within 60 minutes or the AO-approved time. False alarms are limited to one per 30 days per partition, and service starts within four hours of a trouble signal. Testing is semiannual. Put these on the cover sheet of your IDS submittal with the paragraph cited beside each.

## Slide 14
14 · UL 2050
UL 2050 and “Extent 3” explained
Sources: IC Tech Spec 7.A.2 · UL CS-ASD-NISS instructions · 32 CFR 117.15(d)(4) · CDSE SA501 · ICS 705-1
14 / 24
“Extent” = how much of a space an alarm covers.
Tech Spec 7.A.2.b: “Installation shall comply with an Extent 3 installation as referenced in UL 2050.”
Extent 3
Required for every SCIF and SAPF
The highest level for National Industrial Security Systems
ICD 705 adds Level II door switches plus motion, 24 h power and encrypted signals
Extent 5
A reduced level based on patrols and Security-in-Depth
Needs CSA approval under 32 CFR 117.15
No Extent 5 option in the Tech Spec: never for a SCIF or SAPF
CERTIFIES THE COMPANY
UL 2050 certifies the alarm company, not a product.
Edition 6
7 Apr 2025
CRZH
Alarm service company listing
CRZM
Monitoring station listing
Certificate
Kept current; renewed after any IDS change
Trap: web glossaries that rank “Extent 1–5” with 5 as complete coverage are wrong. Extent is not a TEMPEST, RF or acoustic rating.
Notes: “Extent” is UL’s word for how much of a space the alarm protects. Tech Spec 7.A.2.b requires an Extent 3 installation as referenced in UL 2050, for every SCIF and SAPF; CDSE calls Extent 3 the highest level for National Industrial Security Systems. Extent 5 is a reduced, patrol-based level that needs CSA approval under the NISPOM and never applies to a SCIF or SAPF. UL 2050 Edition 6 certifies the alarm service company, listed under CRZH, and monitoring stations under CRZM; it does not certify products. Contractor SCIFs keep a current certificate and renew it after IDS changes. Verify listings in UL Product iQ, and use licensed copies of the standard rather than web summaries.

## Slide 15
15 · ACCESS CONTROL
Access control and identity
Sources: ICS 705-1 §G.2.b · FFC v1.5 §C.1 · UFC 4-010-05 · NIST FIPS 140-3 transition · Hirsch datasheets
15 / 24
Card something you have
PIN something you know
Biometric optional
Reader + keypad, tamper-protected
FIPS-validated encryption
Inside the SCIF or a SECRET-controlled, alarmed area
Controller
Head-end server
RULES THAT FAIL INSPECTIONS
Two technologies at the door. “Card only” mode is single-factor, whatever the reader can do.
Access control never secures an empty SCIF.
ID data and PINs restricted to SCI-indoctrinated staff.
FIPS 140-2 moves to NIST’s historical list on 21 Sep 2026: ask for FIPS 140-3.
PLATFORM EXAMPLE · HIRSCH
Mx controllers: UL 294 and UL 1076 listed
FIPS 140-3 certified cryptography with TLS 1.3 (per Hirsch)
TS ScramblePad readers scramble digits on every use
Two-person rule, occupancy counting, door interlocks
Velocity integrates with DMP XR-series intrusion panels
Manufacturer claims, not AO approvals.
Notes: During duty hours, a SCIF entrance must verify at least two technologies, such as a card plus a PIN. What counts is how the door is configured, not what the reader can do. Readers outside the SCIF must be tamper-protected, lines leaving protected space need FIPS-validated encryption, and the head-end must sit inside the SCIF or in a SECRET-controlled, alarmed area. FIPS 140-2 validations move to NIST’s historical list on 21 September 2026, so ask for 140-3 on new work and confirm with your AO. As one platform example, Hirsch states its Mx controllers are UL 294 and UL 1076 listed and use FIPS 140-3 cryptography, and its ScramblePad readers scramble keypad digits. These are manufacturer claims; the AO approves the design.

## Slide 16
16 · NESTED AREAS
Nested access: higher → lower, never lower → higher
Sources: UFC 4-010-05 3-3.3.2 · IC Tech Spec 2.C · E.O. 13526 §4.1 · NIST SP 800-116 Rev. 1
16 / 24
B1 · BUILDING OR FLOOR
Card
B2 · COLLATERAL AREA
Card + PIN
B3 · SCIF
2+ technologies
B4 · COMPARTMENTED AREA
Program read-in
✓ Outward: allowed, with a grant at each door
✕
Inward without access: denied; escort only
Higher → lower: allowed
People cleared for an inner area may use outer doors, with an explicit grant at each one.
Lower → higher: never
An outer-area grant opens nothing inside. Visitors are escorted.
DESIGN RULES
Put high inside low: never enter a lower area through a higher one
Authentication factors never decrease going inward
Clearance isn’t access: eligibility, NDA, need-to-know
Compartmented area doors: no spin-dial locks, no separate alarm
Notes: Secure spaces nest like boxes: the building, a collateral area, the SCIF, and perhaps a compartmented area inside it. The rule of thumb is one-way. People with access to an inner, higher area may walk outward through lower areas, as long as each door has its own explicit grant. People with only outer access never gain entry inward; inside, they are escorted. UFC 4-010-05 says entry into a lower security area cannot be through a higher one, so lay out high inside low. Authentication factors should never decrease going inward. Clearance alone isn’t access: it takes eligibility, a signed nondisclosure agreement and need-to-know. The Tech Spec also bars spin-dial locks and independent alarm systems on compartmented areas.

## Slide 17
17 · TEMPEST BASICS
RED/BLACK basics
Sources: UFC 4-010-05 3-3.3.2, 3-4.19 · IC Tech Spec 3.A.3 · NACSIM 5000 (historical) · NSA declassified history
17 / 24
RED
Classified information in the clear
Classified computer and monitor
The cable between them
Unencrypted classified circuits
BLACK
Encrypted or unclassified only
Building power and phones
Unclassified LAN, fire alarm, building controls
IDS, access control, CCTV
SEPARATION SET BY YOUR CTTA
Keep RED physically and electrically apart from anything BLACK that leaves the room.
Label everything
Cabling, patch panels, outlets and connectors marked by classification
Separate pathways
Never share a bundle, tray or patch panel. Don’t improvise reroutes.
Keep crypto close
Encryption gear in telecom rooms within or next to the secure area
Review first
The CTTA decides countermeasures; grounding is engineered, not improvised
Notes: RED means equipment, wires and signals carrying classified information in the clear, like a classified computer and the cable to its monitor. BLACK means anything carrying only encrypted or unclassified information: building power, phones, the unclassified LAN, fire alarm, and the IDS, access control and CCTV systems. RED/BLACK discipline keeps RED signals from coupling onto BLACK conductors that leave the room. TEMPEST is a covername, not an acronym. The CTTA decides which countermeasures a facility needs, and separation distances come from that review and your drawings; we do not publish them. Installers can still do the basics: label everything, keep pathways separate, keep encryption equipment close to the secure area, and never buy countermeasures before the review.

## Slide 18
18 · EMI FILTERS
EMI filters: line outside, load inside
Sources: ETS-Lindgren filter manual · Premier EMC installation guidance · IC Tech Spec 3.G. Levels come from your CTTA.
18 / 24
RF SHIELD
OUTSIDE · UNPROTECTED
INSIDE · PROTECTED ROOM
LINE · dirty
LOAD · clean
Panel
LINE
LOAD
Branch circuits
1
Feeder ends at LINE side
2
Case bonded metal-to-metal to the shield
3
LOAD conductors through a gasketed penetration
4
Test the finished room
Backwards fails
Unfiltered conductors end up inside the room, where RF radiates and signals can couple onto them.
A shared box fails
Dirty and clean wires in one box or raceway let RF jump around the filter entirely.
Filters store charge
Lock out and tag out, wait, verify with a meter, then use a shorting stick.
Notes: A power-line filter is a sieve for electricity: 60-hertz power passes, and radio-frequency energy riding on the wires is diverted to the filter case and into the shield. It only works if it is installed the right way round. The feeder from the building panel ends at the LINE, or dirty, compartment outside the shield. The filter case is bonded metal-to-metal to the shield. LOAD, or clean, conductors enter the room through a gasketed penetration. Then the finished room is tested. Reverse it and unfiltered conductors run inside the room. Share a pull box between dirty and clean wires and RF jumps around the filter. Filters also store charge, so lock out, wait, verify and discharge before touching one.

## Slide 19
19 · SHIELD PENETRATIONS
Shield penetrations: breaks, waveguides and fiber
Sources: IC Tech Spec 3.G.2 · UFC 4-010-05 3-4.11.2 · Holland Shielding · In Compliance Magazine (2022)
19 / 24
Non-shielded perimeter: break the metal path, only if the CTTA directs
RF-shielded room: bond metal to the shield; size openings as waveguides
METAL
BREAK
METAL
Dielectric break
A short, listed non-metal section: union, flange kit or duct connector
Stops metal acting as a long wire out of the room
Length and location come from the CTTA and drawings
Listed and firestopped for the system it serves
RF
AIR / WATER
Waveguide-beyond-cutoff
A narrow metal tube passes air, water or fiber; RF below cutoff dies out
Opening size sets the cutoff; length sets the attenuation
Never a conductor through it: that makes a coax with no cutoff
Honeycomb vents apply the same idea to HVAC air
MC
MC
FIBER
Fiber entry
Convert to light; run all-dielectric fiber through a waveguide
No armor, steel strength member or tracer wire
Converters inside on filtered power; never PoE or copper
Size tubes for spares: adding one later means a retest
Notes: Every metal item that crosses the boundary can carry signals, and the treatment depends on the boundary. At a normal, non-shielded SCIF perimeter, the CTTA may direct a dielectric break: a short, listed non-metal section that stops a pipe, conduit or duct acting as a long wire. Its length comes from the CTTA and the drawings. At an RF-shielded room the logic reverses: metal is bonded to the shield, and openings are sized as waveguides. A narrow tube passes air, water or fiber while RF below its cutoff frequency dies out; length sets the attenuation. Never pass a conductor through a waveguide. For data, convert to light, use all-dielectric fiber, and power the converters from filtered circuits. MC on the slide means media converter.

## Slide 20
20 · INSTALLER METHODS
Never fasten through the shield
Sources: IC Tech Spec 3.G.5 · UFC 4-010-05 3-4.4.7 · MIL-HDBK-1195 (historical) · In Compliance Magazine
20 / 24
WALL SECTION
OUT
SCIF
✕
Wrong: a screw, anchor or hanger through the shield leaves a hole RF leaks through
✓
Right: a furred wall on stand-offs, or surface raceway; fasteners stop short of the shield
Leaks can’t be seen, only measured. Any new penetration means review, then retest.
Do
Surface-mount, use raceway, or build a furred wall
Mount door switches on maker brackets on the protected side
Route low-voltage cable to the single entry point
Report an accidental hole: vendor repair, then retest
Don’t
Drive screws, anchors, powder pins or hanger rods through foil or steel
Recess boxes or panels in a perimeter wall
Caulk over a shield hole
Pass copper, PoE or steel-member fiber through a waveguide
Notes: An RF shield only works as a continuous metal skin, so every screw, anchor, powder-actuated pin or hanger rod that pierces the foil or steel creates a leak. Tech Spec 3.G.5 says utility distribution on the inside of an acoustically or RF-treated perimeter wall is surface-mounted, run in raceway, or carried on an added wall built on furring strips as stand-offs. In practice: no flush boxes in the shielded wall, no TVs anchored straight through it, and door switches mounted on the manufacturer’s brackets on the protected side. Route low-voltage cable to the single entry point. If someone does puncture the shield, don’t caulk over it: report it, let the shield vendor repair it, and retest.

## Slide 21
21 · PEDS AND TELECOM
PEDs, detection and telecom
Sources: ICS 705-1 §G.2 · UFC 4-010-05 3-4.7, 3-4.17.2 · SECDEF memo (30 Jun 2023) · FFC v1.5 §F–G
21 / 24
Portable devices
PEDs pose a risk to SCI; the AO approves any exception
No RF transmitters inside unless evaluated, mitigated and AO-approved
Lockers outside the primary entrance, at least 10 ft from unencrypted classified processing
Medical devices get an individual review
Device detection
DoD directed SCIFs and SAPFs to program for detection systems (SECDEF memo, June 2023)
RF detectors only see devices that are transmitting
Powered-off phones are invisible; airplane mode can leave Wi-Fi and Bluetooth on
Detection feeds access control and must never block egress
Telecom and CCTV
Unclassified phones: TSG-6 (CNSSI 5006) approved phone or disconnect device
Speakerphones and microphones disabled unless AO-approved
PA and notification: no audio back feed
Cameras stay outside and never view inside; keypads out of frame
Integrator note: detectors, sensors and speakers are equipment too. Anything inside the SCIF or crossing the perimeter needs AO review, and CTTA review where TEMPEST applies.
Notes: Portable electronic devices are one of the most common real-world risks. ICS 705-1 says PEDs pose a risk to SCI, and RF transmitters are not allowed inside unless a competent authority evaluates and mitigates them and the AO approves. DoD criteria put lockable PED cabinets outside the primary entrance. In June 2023, the Secretary of Defense directed components to program for electronic device detection in SCIFs and SAPFs. Detection has limits: RF sensors only see transmitting devices, and powered-off phones are invisible. For telecom, unclassified phones need CNSSI 5006 approved instruments or disconnect devices, microphones and speakerphones are disabled unless approved, and paging systems must not feed audio back out. Cameras stay outside the perimeter.

## Slide 22
22 · TOP TRAPS
Top traps that fail inspections
Sources: IC Tech Spec · UFC 4-010-05 · FFC v1.5 · shielding and filter manufacturer guidance · practitioner reports
22 / 24
TRAP 01
AO engaged after design or contracts
Coordinate first; no award without an approved CSP
TRAP 02
Walls stop at the drop ceiling
Build true floor to true ceiling, sealed
TRAP 03
Wall A for open storage, assuming SID
Settle the SID decision before drawing walls
TRAP 04
“Card only” mode on a card + PIN reader
Configure and document two factors
TRAP 05
Access control server in unsecured space
Head-end in the SCIF or an alarmed SECRET area
TRAP 06
VTC added to a Sound Group 3 room
Zone Sound Group 4 rooms during design
TRAP 07
Filter reversed, or wires sharing a box
Dirty side outside, clean side inside, kept apart
TRAP 08
A new penetration after the shield test
Freeze the schedule; review and retest
Notes: These eight traps show up again and again. Engaging the AO after design or contracts forces rework, and awarding a contract without an approved Construction Security Plan violates the Tech Spec. Walls that stop at the drop ceiling fail both the true-ceiling and acoustic requirements. Designing Wall A for open storage before SID is accepted can leave you needing enhanced walls and a 5-minute response. A card-plus-PIN reader running in card-only mode is a single-factor door. Access control head-ends belong inside the SCIF or a SECRET-controlled alarmed area. Adding VTC to a Sound Group 3 room breaks compliance. And on shielded rooms, reversed filters and late penetrations invalidate the test. Each has a simple fix if caught early.

## Slide 23
23 · GETTING STARTED
How to start a SCIF project
Sources: IC Tech Spec 2.A, 3.A–3.B · UFC 4-010-05 · UL Product iQ · KB synthesis. Your AO’s direction controls.
23 / 24
1
Confirm the mission need and sponsor
DoD SCIFs need a SCIF number or written concept approval.
2
Identify the AO and appoint an SSM
Talk to the AO before design, orders or contracts.
3
Profile the facility
Storage mode, Security-in-Depth, U.S. or overseas.
4
Zone every room
Sound Group 3, Sound Group 4 or non-discussion.
5
Get the CTTA’s review early
Submit the TEMPEST checklist; buy no filters or shielding before the review.
6
Build a penetration schedule
Every duct, pipe, conduit and cable, entering at a single point.
7
Bring in your IDS and ACS integrator
Verify UL 2050 listings (CRZH and CRZM) in UL Product iQ.
8
Approve the CSP before award
Then build under surveillance and photograph everything before cover.
Notes: Here is a practical way to start. First, confirm the mission need and your government sponsor; DoD SCIFs need a SCIF number or written concept approval. Identify the AO early and appoint a Site Security Manager, and talk to the AO before design, material orders or contracts. Profile the facility: storage mode, Security-in-Depth and location. Zone every room for Sound Group 3, Sound Group 4 or non-discussion. Submit the TEMPEST checklist and wait for the CTTA’s review before buying countermeasures. Build a penetration schedule with a single point of entry. Bring your IDS and access control integrator in during planning, and verify its UL listings. Finally, get the Construction Security Plan approved before contract award.

## Slide 24
24 · RESOURCES
Resources and contact
24 / 24
PUBLIC REFERENCES
ICD 705 · ICS 705-1 · ICS 705-2
ODNI / NCSC
IC Tech Spec v1.5.1 and forms
ODNI / NCSC
UFC 4-010-05 (2023)
DoD design criteria
DoDM 5205.07 (2025)
DoD SAP security manual
FF-L-2740B · FF-L-2890C · QPL
DoD Lock Program
UL 2050 certificates
UL Product iQ
SCIF ANSWERS KNOWLEDGE BASE
lacctvsupply.com/scif-answers.php
Call 1-626-789-2267 · lacctvsupply.com
Low-voltage scope for secure spaces: intrusion detection, access control, entrance video and cabling.
Public-level educational information only. It does not replace the direction of your Accrediting Official, Cognizant Security Authority or CTTA, engineered drawings, the NEC or your AHJ. No product is “ICD 705 certified”: the AO accredits the facility. Final system design, IDS/access control integration and door hardware are subject to AO/CSA approval, and CTTA approval where TEMPEST applies.
Notes: To go deeper, start with the public documents: ICD 705 and its two standards, the IC Tech Spec version 1.5.1 with its forms, UFC 4-010-05 for DoD design criteria, DoDM 5205.07 for SAP work, the DoD Lock Program for approved locks and door hardware, and UL Product iQ to verify alarm company and monitoring station listings. LA CCTV Supply’s SCIF Answers knowledge base at lacctvsupply.com expands every topic in this briefing with sources. A final reminder: this is general, public-level education. Your AO, CSA and CTTA set the requirements for your facility, and no product is ICD 705 certified. The AO accredits the facility, based on how it is designed, built, tested and run.